## Slide 1: Thermal analysis of the diam loop in HM31 and Baffle module 9v analysis
Mikhail Khokhlov
Vojtěch Smolík

## Slide 2: Introduction
Workbench simulation is developed to examine radiation heat load to diam loop in HM31
Cooling water is simulated as a thermal liquid beam –temperature increase along the channel
Steady-state simulation
Uniform heat flux

## Slide 3: Boundary conditions
Materials
    Material properties imported from W 7-X library
Initial temperatures and flow rates
    Inlet temperature 30 °C , pipe convection 17 000 W/m2C
    flow rates predicted by KiP: Hydraulic calculation of 1st wall cooling loops (OP1 and OP2) 29HDQV v2.0
Heat flux
    Uniform heat flux by Specification of Design Loads for In-vessel Components of W7-X 2AYMBW + solution
Radiation towards PV
    Ambient temperature used for radiation solver: 30 °C

## Slide 4: Results: cooling water heat up
 | DT [K] predicted by 29HDQV v2.0 | DT [K] Workbench result 250 kW/m2 | DT [K] Workbench result 150 kW/m2 | Flow rate [l/s]
H77 1-ACH31AC610b | 10 | 18,5 | 11,1 | 0,48
H34 1-ACH31AC560b | 16 | 27,1 | 16,4 | 0,45
H81 1-ACH31AC570b | 19 | 27,1 | 16,4 | 0,7
H81 1-ACH31AC570b
H34 1-ACH31AC560b
H77 1-ACH31AC610b

## Slide 5: Results temperatures in HSs - 250 kW/m2

## Slide 6: Results temperatures in HSs - 150 kW/m2

## Slide 7: Results temperatures in HSs - 250 kW/m2

## Slide 8: Results temperatures in HSs - CuCrZr - 250 kW/m2

## Slide 9: Results: Heat balance & radiation towards PV – 250 kW/m2
 | PF heat [W] | Ratio of PF heat | Area [m2] | avg. rad. heat flux [W/m2]
PF heat | 171 172,5 | 100% | 0,68469 | 
Convection - cooling pipes | -167658 | 97,9% | 0,24492 | -
Convection - in/outlet areas of cooling pipes | -104,44 | 0,06% | 0,00999 | -
Radiation – graphite | -3116,9 | 1,82% | 0,25607 | 12172
Radiation – CuCrZr | -231,654 | 0,13% | 0,28789 | 804
Radiation – pipes | 106,431 | 0,06% | 0,14005 | 760
Radiation – connector plates | -111,531 | 0,06% | 0,10799 | 1032
Conduction – supports to vessel | -26,7 | 0,01% | 0,0007 | -
SUM | 29,66 | - |  | 4234,41

## Slide 10: Results: Heat balance & radiation towards PV – 150 kW/m2
 | PF heat [W] | Ratio of PF heat | Area [m2] | avg. rad. heat flux [W/m2]
PF heat | 102 703,5 | 100% | 0,68469 | 
Convection - cooling pipes | -101 494 | 98,8% | 0,24492 | -
Convection - in/outlet areas of cooling pipes | -63,3 | 0,06% | 0,00999 | -
Radiation – graphite | -1014,11 | 1,8% | 0,25607 | 3960
Radiation – CuCrZr | -96,38 | 0,13% | 0,28789 | 334
Radiation – pipes | -39,07 | 0,03% | 0,14005 | 279
Radiation – connector plates | -45,19 | 0,04% | 0,10799 | 418
Conduction – supports to vessel | -26,7 | 0,04% | 0,0007 | -
SUM | -17,04 | - |  | 1409

## Slide 11: PV Heat flux – without bolts connecting HS to PV- 250 kW/m2

## Slide 12: PV Heat flux – without bolts connecting HS to PV - 150 kW/m2

## Slide 13: PV Temperature – with bolts connection to the PV
250 kW/m2
150 kW/m2

## Slide 14: PV added to the simulation
PV cooling water (250 kW/m2)

## Slide 15: Welding the PV cooling pipes
Actual geometry
Simplified geometry used for solution

## Slide 16: PV with cooling pipes - temperature profile

## Slide 17: Baffle module 9v transient analysis
to evaluate the relation between heat sink thermocouple measurements and heat flux load
surface temperature measurements of BM 9v available

## Slide 18: Importing the temperature profile of graphite surface

## Slide 19: Issue #1 - Bolts positions are not properly matching

## Slide 20: Imported surface temperature profile
Visible convective load area

## Slide 21: Thermocouple results validation
Thermocouple temperature – experimental vs simulation

## Slide 22: Issue #2 – How to evaluate the heat flux profile

## Slide 23: Heat flux results – average per tile

## Slide 24: Questions
Sigraflex thermal conductivity
BM_materials definition:
(used for presented sim.)
SGL carbon manufacturer :
3 W/mC
The quality of thermal contact between sigraflex and graphite/crcrzr

## Slide 25: Comparison one tile Workbench vs. Fluent - 250 kW/m2
Workbench
Fluent

## Slide 26: Questions
Film coefficient for water cooled pipes, reference: Heat transfer coefficients for turbulent pipe flows, Andre Carsl, 1-ACH00AC400 , -T0002.0
- used coeff.: 17 000 W/mK
Fluent result - HTC
HTC 10 500 W/m2/K applied to Workbench simulation = Workbench results match Fluent simulation

## Slide 27: Zyklischer Belastungstest einer Baffle-Probe

## Slide 28: Questions
INLET / OUTLET positions
INLET
INLET
INLET

## Slide 29: Questions
Thermocouple measurement data and positions
    do we really have thermal sensors only in the tip of triangle shaped area?